## Outback
Radian / FXR / VFXR Inverter Settings
Inverter | Compact Series | Stack'd Series
Absorb Voltage and Time | 56 Vdc/ 0.1hr | 52.5 Vdc/ 0.1hr | 3.5 | 56 | 52.5
Float Voltage and Time | Default |  | 3.45 | 55.2 | 51.75
| (Disable the Float charge by setting Float Time to 0) |  | #REF! | #REF! | #REF!
EQ Voltage and Time | Default
(Disable the Equalization charge by setting EQ Time to 0)
Re-float Voltage | Default |  | 3.3 | 52.8 | 49.5
| (Disable the Float charge by setting Float Time to 0) |  | #REF! | #REF! | #REF!
Re-Bulk Voltage | 50.8 Vdc | 47.6 Vdc | 3.175 | 50.8 | 47.625
AC Charger Limit in AC @240VAC | 25 Aac per Compact | 23 Aac per module | #REF! | #REF! | #REF!
|  | (Limited to 70Aac per Homegrid Controller) | #REF! | #REF! | #REF!
Low Battery Cut-Out Voltage | 50V | 46.9V | #REF! | #REF! | #REF!
LBCO Delay | 130 seconds |  | #REF! | #REF! | #REF!
Low Battery Cut-in Voltage | 52V | 48.7V | 3.25 | 52 | 48.75
High Battery Cut-Out Voltage | 56.8V | 53.2V | 3.55 | 56.8 | 53.25
HBCO Delay | 10 seconds |  | #REF! | #REF! | #REF!
High Battery Cut-in Voltage | 54V | 50.7V | 3.38 | 54.08 | 50.7
Sell_RE Voltage | 54V | 50.7V | #REF! | #REF! | #REF!
Temp Sensors | Do not use temperature sensors / reduce any temperature coefficients to as close to zero as allowed |  | #REF! | #REF! | #REF!
Outback Skybox Settings under the Custom choice
Inverter | Compact Series | Stack'd Series
Maximum SOC | 100%
Minimum SOC | 20%
Absorb Charge | Timed
Absorb Voltage | 56 Vdc | 52.5 Vdc
Absorb Time | 00:06 hr
Float Charge | Disabled | Disabled
Float Voltage | Can be left at default | Can be left at default
Float Time | Can be left at default | Can be left at default
Re-float Voltage | Can be left at default | Can be left at default
Re-bulk Voltage | 50.8 Vdc | 47.6 Vdc
Equalize Voltage | Can be left at default | Can be left at default
Minimum Equalize Time | 00:00 hr | 00:00 hr
Max Charge Current (Adc) | 100Adc per Compact | 100Adc per module
(Limited to 300Adc per Homegrid Controller)
Max Discharge Current (Adc) | 100Adc per Compact | 100Adc per module
(Limited to 300Adc per Homegrid Controller)
Grid Charge Limit (kW) | Site specific | Site specific
Low Battery Cutout | 50 Vdc | 46.9 Vdc
LBCO Delay | 130 seconds | 130 seconds
Low Battery Restart | 52 Vdc | 48.7 Vdc
High Battery Cutout | 56.8 Vdc | 53.2 Vdc
HBCO Delay | 10 seconds | 10 seconds
High Battery Cut-in | 54 Vdc | 50.7V
Battery Series | Custom | Custom
Battery Model Number | Custom | Custom
Battery Description | Homegrid | Homegrid
Battery Total Amp-Hours | 100Ah per Compact | 100Ah per module
Charge Efficiency Factor | 0.98 | 0.96
Absorb End Amps | 2 Adc | 2 Adc
FM60/80/100 Charge Controller Settings
Charge Controller | Compact Series | Stack'd Series
Absorb Voltage and Time | 56.3V, 0.1 hours | 52.8V, 0.1 hours | 3.52 | 56.32 | 52.8
Float Voltage | 54V | 50.7V
Rebulk Voltage | 51.2 Vdc | 48 Vdc
DC Current Limit | 100A per Compact ÷ # of Outback controllers | 100A per battery ÷ # of Outback controllers
(Limited to 300Adc per Homegrid Controller ÷ # of Outback controllers)
Absorb End Amps | 2 Adc
FN-DC | Compact Series | Stack'd Series
Battery Ah | 100Ah per Compact | 100Ah per module
Charged Voltage | 54V | 50.7V
Charged Time | 1 min
Charged Return Amps | 2 Adc
MATE3s | Compact Series | Stack'd Series
FN-DC Advanced | Low SOC Warning = 20%
FN-DC Advanced | Critical SOC Warning = 10%